ROOT CAUSE ANALYSIS REPORT P-101 · Boiler Feedwater Pump P-101

Event Date: 14 March 2026

Report ID: RCA-2026-0314-001

Report Generated: 23 May 2026

Document Control

| Equipment ID | P-101 |
| --- | --- |
| Equipment Name | Boiler Feedwater Pump P-101 |
| Event Date | 14 March 2026 |
| Report ID | RCA-2026-0314-001 |
| Generated | 23 May 2026 |
| Site | Kwinana Process Facility |
| Investigation Lead | Reliability Engineering Team |

Executive Summary

On 14 March 2026, boiler feedwater pump P-101 tripped on high vibration after catastrophic failure of its inboard mechanical seal, releasing hot treated feedwater and forcing a 72-hour unplanned outage of No. 2 boiler. This was the third seal failure on P-101 in 14 months. The immediate cause was dry-running of the seal faces during a low-flow transient. The root cause was the absence of minimum-flow protection: a recirculation line isolated during a 2024 modification was never reinstated, and no low-flow trip was configured. The change passed through management of change without a hazard review of the lost protection. Five corrective actions are recommended, two of which address the root cause directly.

1. Problem Statement

Pump P-101 inboard mechanical seal failed catastrophically at 02:14 on 14 March 2026, causing loss of containment of treated feedwater, a high-vibration trip, and a 72-hour forced outage of No. 2 boiler. Estimated combined repair and lost-production impact is A$340,000.

2. Business Impact

| Downtime | 72 hours (forced outage) |
| --- | --- |
| Lost Production | ~1,850 t steam equivalent |
| Cost Impact | A$340,000 (repair + lost production) |
| Safety Impact | Hot feedwater release; no injury, but exposure potential rated HIGH |
| Quality Impact | Boiler water chemistry excursion during restart |
| Repeat Failure Status | Third seal failure on P-101 in 14 months (Jan 2025, Aug 2025, Mar 2026) |

3. ISO 14224 Asset Taxonomy

| Equipment ID | P-101 |
| --- | --- |
| Equipment Class | Pumps (PU) — ISO 14224 |
| Sub-Class | Centrifugal, single-stage (BB1) |
| Failure Mode | ELP — External Leakage, Process Medium |
| Failure Mechanism | Seal-face dry-running / thermal cracking |
| Failure Severity | Critical |

4. Evidence and Observations

Evidence Register

| # | Evidence Item | Type | Classification | Key Finding |
| --- | --- | --- | --- | --- |
| E1 | Failed inboard seal faces (SiC vs carbon) | Physical — metallurgical exam | DIRECT | Heat-checking and radial thermal cracks on both faces, consistent with dry-running |
| E2 | DCS trend 02:00–02:14 | Process data | DIRECT | Discharge flow held below 18% BEP for ~6 minutes before the vibration spike |
| E3 | P&ID rev 2024-C | Document | INDIRECT | Minimum-flow recirculation line shown isolated; no low-flow trip configured |
| E4 | MOC-2024-087 record | Document | DIRECT | 2024 modification removed the recirc line; no seal or low-flow hazard review recorded |
| E5 | Operator interview (night shift) | Testimonial | INDIRECT | No alarm prompted action; low-flow condition not recognised in time |

Evidence Gaps

| # | Gap | Why It Matters | How to Resolve |
| --- | --- | --- | --- |
| G1 | Seal flush flow rate during the event | Flush flow is not historised | Add seal-flush flow to the DCS historian and install a local low-flow switch |
| G2 | Exact duration below minimum continuous stable flow over prior weeks | Low-flow excursions not trended or alarmed | Configure a low-flow alarm and capture excursion statistics |

5. Fishbone Analysis — All Possible Causes

Equipment

• Inboard seal faces ran dry

• Minimum-flow recirculation not in service

• Seal flush (API 682 Plan 11) marginal at low flow

People

• Night operator did not recognise the low-flow condition

• No alarm to prompt intervention

Process/Method

• Low-flow transient during a boiler swing

• No low-flow protection trip

• Start-up procedure lacks a minimum-flow check

Environment

• Elevated feedwater temperature reduces seal margin

Management System

• 2024 MOC removed protection without hazard review

• Repeat-failure trend not escalated to RCA

• Seal not held as a critical spare

Material

• Carbon face susceptible to thermal shock when run dry

6. Pareto Ranking — Priority Causes

| Rank | Category | Cause | Classification |
| --- | --- | --- | --- |
| 1 | Management System | Minimum-flow protection removed via MOC without a hazard review | Root |
| 2 | Process/Method | No low-flow trip and no recirculation in service | Root |
| 3 | People | Low-flow condition not detected in time | Contributing |
| 4 | Equipment | Seal flush marginal at low flow | Contributing |

7. Five-Why Drill-Down

Cause 1: Inboard mechanical seal failed

| Level | Answer | Classification |
| --- | --- | --- |
| Why 1 | Seal faces ran dry and thermally cracked | CONFIRMED |
| Why 2 | Pump operated below minimum continuous stable flow | CONFIRMED |
| Why 3 | No minimum-flow recirculation in service and no low-flow trip | CONFIRMED |
| Why 4 | Recirculation line was isolated in the 2024 modification and never reinstated | CONFIRMED |
| Why 5 | The MOC did not assess the loss of low-flow protection | CONFIRMED |

Root Cause (CONFIRMED) The MOC process did not require a seal / low-flow protection hazard review for changes to pump auxiliary systems

8. Root Cause Statement

Root Cause 1 — CONFIRMED Minimum-flow protection (recirculation + trip) was removed under the 2024 MOC without a hazard review, leaving P-101 unprotected against low-flow dry-running.

Root Cause 2 — PROBABLE Repeat seal failures were not escalated to a formal reliability investigation after the first two events.

9. Barrier Analysis (Tripod Beta / Bowtie)

Preventive Barriers

| # | Barrier | Type | Status | Evidence |
| --- | --- | --- | --- | --- |
| P1 | Minimum-flow recirculation line | Engineered | MISSING | Isolated in 2024, not reinstated |
| P2 | Low-flow protection trip | Instrumented | MISSING | Not configured in the DCS |
| P3 | Seal flush plan (API 682 Plan 11) | Engineered | INADEQUATE | Marginal flush at low flow |

Mitigative Barriers

| # | Barrier | Type | Status | Evidence |
| --- | --- | --- | --- | --- |
| M1 | High-vibration trip | Instrumented | EFFECTIVE | Tripped the pump and limited consequential damage |
| M2 | Bunding and drainage | Engineered | EFFECTIVE | Contained the feedwater release |

10. Root Cause Validation (Counterfactual Test)

| Root Cause | Counterfactual Result | Residual Risk |
| --- | --- | --- |
| Missing minimum-flow protection | Confirmed by DCS trend, P&ID and MOC record | HIGH until reinstated |
| Failures not escalated | Confirmed by absence of prior RCA records | MEDIUM |

11. Action Plan

| # | Category | Action | Owner | Due | HOC Level |
| --- | --- | --- | --- | --- | --- |
| A1 | IMMEDIATE | Restrict P-101 to >40% BEP; brief operators; manual recirculation via spare line | Operations Superintendent | Completed 15 Mar 2026 | Administrative |
| A2 | ROOT CAUSE | Reinstate the minimum-flow recirculation line and commission an automatic low-flow trip | Projects / Reliability | 30 Apr 2026 | Engineered |
| A3 | ROOT CAUSE | Revise the MOC procedure to mandate a protection-impact review for pump auxiliary changes | Engineering Manager | 31 May 2026 | Management system |
| A4 | CONTRIBUTING | Upgrade seal flush to API 682 Plan 11+13 and historise flush flow | Reliability Engineer | 30 Jun 2026 | Engineered |
| A5 | GOOD TO HAVE | Add the P-101 seal cartridge to critical-spares holding | Maintenance Planner | 30 Jun 2026 | Management system |

Success Criteria and Verification

| # | Success Criterion | Verification Method |
| --- | --- | --- |
| A1 | No operation below 40% BEP | DCS flow audit |
| A2 | Recirculation in service and trip function-tested | Commissioning and SAT records |
| A3 | MOC template includes a protection-impact checklist | Procedure audit |
| A4 | Flush flow trended and alarmed | DCS configuration review |
| A5 | Spare seal held in store | CMMS stock check |

12. Extent of Condition / Generic Implications

| Domain | Status | Note |
| --- | --- | --- |
| Sister pumps P-102 / P-103 | ACTIVE | Verify minimum-flow protection is in service on all boiler feedwater pumps |
| Other 2024 MOC changes | ACTIVE | Review for protections removed without a hazard review |
| Cooling-water pumps | NOT APPLICABLE | Different duty; low-flow dry-running risk is low |

13. Learning System Assessment

Finding Removing a protective device through MOC without a hazard review reintroduced a known failure mode.

Learning System Root Cause

MOC scope did not cover loss of protection on auxiliary systems.

Precursor Signal Timeline

| Day | Event |
| --- | --- |
| Jan 2025 | First P-101 seal failure — treated as routine maintenance, no investigation |
| Aug 2025 | Second seal failure — seal replaced, still no RCA |
| Mar 2026 | Third failure — finally escalated to a formal RCA |